BUILDING

Footing:

To be made after trenches are excavated and the necessary reinforcement and forms are in place and before concrete is placed.  Drilled footings, piles and similar types of foundations shall be inspected as installed.  (A portable toilet facility to be in place before excavation begins.

Slab:

To be made after all plumbing, mechanical, wiring and moisture barrier are in place; termite treatment to be completed.

Foundation:

To be made after foundation wall or spot piers have been erected and prior to any structural framing; termite treatment to be completed.

Floor Framing:

To be inspected after all girders and floor joists are in place and before the sub-floor is installed.

Framing:

To be made after all structural framing is in place and all rough-in of electrical, mechanical and plumbing has been installed and inspected, after all fire blocking, chimneys, bracing, vents and brick ties, when required, are installed, but before any of the structure is enclosed or covered.  Poured in place concrete structural elements shall be inspected before each pour of any structural member.

Fireplace:

To be inspected as damper is set and upon completion of chimney on masonry fireplace before removal of scaffolding.

Insulation:

To be made after the building or structure has been roughed-in for electrical, mechanical, plumbing and framing and before sheetrock is installed.

Final:

To be made after the building or structure has all doors hung, fixtures set and ready for occupancy, but before the building is occupied.

ELECTRICAL

Temporary Service Pole:  To be made when set and ready to be energized.

Underground:  To be made after direct burial or conduit is installed, but before it is covered.

Slab:  To be made after all raceway is installed.

Duct Bank:  To be made after raceway is installed, spaced and secured.

Rough-In:  To be made after all wiring and /or raceway are installed, all junction boxes are complete, with covers on, and fire stopping and draft stopping are in place, and before ceiling and wall finish material are installed.

Swimming Pools:  To be made before bonding and grounding is covered.

Final:  To be made after job is complete.

PLUMBING

Slab:  To be made after trenches or ditches are excavated and bedded, piping installed, and before any backfill is put in place.

Rough-in:  To be made after the roof, framing, fire blocking, fire stopping, draft stooping, and bracing is in place and all sanitary, storm and water distribution piping is roughed-in, and before the installation of wall or ceiling finish material.

Water/Irrigation/Sewer Systems: To be made after trenches or ditches are excavated and bedded, piping installed, and before any backfill is put in place.

Final:  To be made after the building is complete, all plumbing fixtures are in place and properly connected, and the structure is ready for occupancy.

MECHANICAL

Underground:  To be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place.  When excavated soil contains rocks, broken concrete, frozen chunks and other rubble, which would damage or break the piping, or cause corrosive action, clean backfill shall be on the job site.

Rough-In:  To be made after the rood, framing, fire blocking, fire stopping, draft stopping, and bracing is in place and all sanitary, storm and water distribution piping is roughed-in, and before the installation of wall or ceiling finish material.

Final:  To be made upon completion of the mechanical and/or gas piping systems.

Note:  Before any system of gas piping is finally put in service, it shall be carefully tested to ensure that it is gas tight.  Where any part of the system is to be enclosed or concealed, this test shall precede the work of closing in.  To test for tightness, the piping shall be filled with air or inert gas.  Oxygen shall never be used for this test.

ORDER OF INSPECTIONS FOR

NEW HOMES

- Footing Inspection

- Foundation inspection, wood frame construction

- Rough-In

- Building framing

- Insulation

- Fire protection

- Final Inspection